Honeycomb Ventilation panels 9500 Series蜂窝通风板系列

Honeycomb ventilation 9500蜂窝通风板

Shielded vent panels for ventilation and heating屏蔽通风板用于通风设备和暖气设备

Honeycomb vents are used to shield openings for heating and ventilation against undesirable electromagnetic waves.

蜂窝通风使用屏蔽孔用于供暖与通风以防止不必要的电磁波。

The aluminium honeycomb vent panels are supplied in rigid aluminium frames, pre-drilled or with fasteners made to your specifications or flow drilled thread holes.

铝制蜂窝通风板的供应用刚性的铝制框架，预钻孔或用夹具做作你的规格或根据流程攻螺纹孔。

If a very high shielding level is required, the use of cross-cell honeycombs is recommended. These are made from two pieces of 6.35 mm or 12.7 mm thick honeycomb within a single frame. The shielding performance will improve at the expense of slightly increased air flow resistance.

如果要求一个非常高的屏蔽级别，推荐使用交叉单元蜂窝。这些由两件6.35mm或12.7mm厚的蜂窝在一个单个的框架内组成。在承担稍微的增加空气流动阻力的情况下屏蔽性能将得到提高。

Standard and cross-cell version标准和交叉单元版本:

(Cross-cell version for higher shielding performance交叉单元版本用于最高的屏蔽性能)

Approximately 95% of the honeycomb vents are made to customer specifications, and are all made to order.

大约95%的蜂窝通风板将根据客户的规格要求进行制造，所有的制造将根据订单。

Standard delivery time: less than two weeks.

标准的交货时间：少于两周。

| Honeycomb ventilation panels蜂窝通风板 | Flanged Honeycombs带凸缘的蜂窝, (See frame type H看框架类型H) |
| --- | --- |

| Honeycomb fan-shields蜂窝风扇屏蔽 | Honeycomb ventilation panels蜂窝通风板 |
| --- | --- |
| Mild steel Vents for EMP低碳钢通风孔用于EMP |  |

Benefits好处

- Light weight 轻重量

- High shielding performance 高的屏蔽效能

- Very low air-flow resistance 非常低的气流阻力

- Reduction of turbulence 减少湍流

Options选件

- Cross-cell honeycomb for extra high shielding performance 交叉单元蜂窝用于极高的屏蔽性能

- Slant honeycomb 30°, 45°, 60° for outdoor rainproof applications (high volume only) 倾斜蜂窝30°, 45°, 60°用于户外防水应用（高容量仅仅）

- Polyurethane filter for dust protection 聚氨酯滤波器用于防护灰尘

- Mechanical protection against damage 机械保护以防损害

- Stainless steel version 不锈钢版本

- Brass 黄铜

Shielding performance屏蔽性能

Airflow characteristics气流特性

Mounting options

Shielding performance屏蔽性能

| Frequency MHz频率 | Mode | Attenuation dB衰减 |
| --- | --- | --- |
| 0.01 | H | 45 |
| 0.1 | H | 49 |
| 1.0 | H | 51 |
| 1.0 | E | >100 |
| 10.0 | E | >100 |
| 100.0 | E | >100 |
| 1000.0 | P | 98 |
| 10000.0 | P | 95 |
| See Guarantee |

Mounting options装配选件

Option选件 1. (Through hole/bolt通孔/螺栓)

Option选件 2. (Flow drilled tap/thread流程钻孔丝锥/攻螺纹)

Standard Dimensions标准尺寸

In the table below some common types are specified to illustrate the required information. Hole diameter P is standard 3.5mm but it ca be delivered in any other size. Also available with screw apertures or inserts.

在下表里一些常用的类型的规格以给出插图需要的信息。孔直径P是标准的3.5mm，但它也能供应为任何其它的尺寸。也可获得以螺丝孔或镶嵌件。

| Outer dimension外部尺寸 | Mounting holes horizontal安装孔水平的 | Mounting holes vertical安装孔垂直的 |
| --- | --- | --- |
| Honeycomb fan shield蜂窝风扇屏蔽 |
| A | B | no | E | no | G |
| 40 | 40 | 2 | 32 | 2 | 32 |
| 60 | 60 | 2 | 50 | 2 | 50 |
| 80 | 80 | 2 | 71 | 2 | 71 |
| 92 | 92 | 2 | 83 | 2 | 83 |
| 120 | 120 | 2 | 105 | 2 | 105 |
| 127 | 127 | 2 | 113 | 2 | 113 |

| Outer dimension外部尺寸 | Mounting holes horizontal安装孔水平的 | Mounting holes vertical安装孔垂直的 |
| --- | --- | --- |
| Honeycomb frame shield蜂窝框架屏蔽 |
| A | B | no | D | E | no | F | G |
| 150 100 200 125 250 150 300 175 350 200 400 250 300 600 | 75 100 100 125 125 150 150 175 175 200 200 250 300 300 | 2 1 3 2 3 2 4 2 4 3 5 3 4 7 | 40 50 20 20 30 25 30 40 40 20 30 30 30 30 | 70 - 80 85 95 100 80 95 90 80 85 95 80 90 | 1 1 1 1 1 2 2 2 2 3 3 3 4 4 | 37.5 50 50 62.5 62.5 25 25 40 40 20 20 30 30 30 | - - - - - 100 100 95 95 80 80 95 80 80 |

Example举例

Most of the honeycomb ventilation panels are made according to customer’s specifications. For standard part number see table above. When ordering honeycomb vents, the following information should be provided:

大多数的蜂窝通风板的制造根据客户的规格。对于标准零件号看上表。当订购蜂窝通风板时，应该提供下列的信息：

| Series系列 | Height高度 (mm) | Width 宽度(mm) | Frame type框架类型 | Drill patern钻孔模型 | Gasket material垫圈材料 |
| --- | --- | --- | --- | --- | --- |
| 9500 | 200 | 200 | C | DS | A |
|  |  |  |  | DS : standard drill patern标准钻孔 DC : custom drill patern定制钻孔 | A : Amucor K : Knitted wire mesh编织线网 N: No gasket material没有垫圈材料 |